## Instructions
Introduction
This calculator will size AIRSYS Fixed Speed WPUs based on the given equipment load, building dimensions, and expected peak outside temperature. The calculation accounts for one extra unit than is needed to provide redundancy in the case of unit failure. If redundancy is not desired, the recommended quanity of WPUs given by this calculator can be reduced by 1. For a detailed hour-by-hour comparison of annual HVAC energy consumption between AIRSYS and other units, please see the Equipment Shelter Utility Calculator.
https://airsysnorthamerica.com/support/equipment-shelter-utility-calculator/
Scope
AIRSYS Fixed Speed, AC Supply Fan, Wall Packaged Units
Input Building Parameters and Outdoor Conditions
1. Open the "Site Conditions" sheet.
2. On the "Site Conditions" sheet, enter values for building dimensions and insulation values. If unsure, leave the default values.
3. Enter values for lighting energy consumption and passive ventilation volume. If unsure, leave the default values.
4. Enter a value for the hottest summer temperature that the site will experience.
5. (Optional) Enter a value for the coldest winter temperature that the site will experience. This is valuable only if the site will require HVAC heating in order to maintain the indoor environment above the minimum set point.
Input Equipment Load
1. Select the approach for entering in the internal equipment heat load. The "Input Units" cell has a drop down list where "DC Power", "kW", and "BTU/h" can be selected. The "DC Power" estimates the heat load using the rectifier output. The "kW" and "BTU/h" options are used when directly entering the heat load
2. Input the required information into the highlighted cell(s). When inputting "DC Power", the output from up to two different DC plants can be inputted and combined.
3. (Optional) Enter the rectifier efficiency. This setting only needs to be changed when inputting "DC Power". The default efficiency is 93%.
Set the Design Margin
1. Open the "Building Results" sheet.
2. Input the desired design margin. The default is 5%.
View Results
Open the "Building Results" sheet. The calculation results and unit recommendation are displayed in the "Recommended Wall Packaged Unit" section

## Site Conditions
Building Parameters Input |  |  | Note:
Highlighted Fields are Adjustable
Building Parameters
Cooling Setpoint | 80 | °F
Heating Setpoint | 50 | °F
Length | 20 | ft |  | DC Power
Width | 12 | ft |  | kW
Height | 9 | ft |  | Btu/h
Wall Insulation R Value | 15 | h·ft2·°F/BTU
Ceiling Insulation R value | 21 | h·ft2·°F/BTU
Floor Insulation R Value | 5 | h·ft2·°F/BTU
Lighting | 50 | W
Passive Ventilation/Leak | 30 | CFM
Design Outdoor Temperature
Hottest Summer Outdoor Temperature | 100 | °F
Coldest Winter Outdoor Temperature | 0 | °F
Equipment Load*
Input Units | kW
DC Float Voltage 1 | 0 | VDC
DC Current 1 | 0 | A
DC Float Voltage 2 | 0 | VDC
DC Current 2 | 0 | A
Rectifier Efficiency | 95% | %
Equipment Load (kW) | 0 | kW
Equipment Load (BTU/h) | 0 | BTU/h
Total Equipment Load (BTU/h) | 0 | BTU/h
*Note: This should only include heatload inside the building (example: heat load from remote radio head should not be included)

## Building Results
Building Load Output |  |  | Note:
Highlighted Fields are Adjustable
[6 empty] | Dropdown: |  | Sizing Table
Sensible Cooling Load |  |  | Heating Load |  |  | 0% | Qty | Size | Rated Sensible Capacity | Derated Sensible Capacity
Heat Gain from Wall/Ceiling/Floor | 1956.5714 | BTU/h | Heat Loss from Wall/Ceiling/Floor | 4891.4286 | BTU/h | 5% | 16 | 18E1C4 (5 Ton) | 843000 | 814400
Heat Gain from Ventilation/Leak | 648 | BTU/h | Heat Loss from Ventilation/Leak | 1620 | BTU/h | 10% | 15 | 18E1C4 (5 Ton) | 786800 | 760100
Heat Gain from Lighting | 170.6 | BTU/h | Heat Gain from Lighting | 170.6 | BTU/h | 15% | 14 | 18E1C4 (5 Ton) | 730600 | 705800
Heat Gain from Equipment | 0 | BTU/h | Heat Gain from Equipment | 0 | BTU/h | 20% | 13 | 18E1C4 (5 Ton) | 674400 | 651500
Total Sensible Cooling Load | 2775.1714 | BTU/h | Total Heating Load | 6340.8286 | BTU/h | 25% | 12 | 18E1C4 (5 Ton) | 618200 | 597200
[6 empty] | 30% | 11 | 18E1C4 (5 Ton) | 562000 | 542900
Design Margin | 5% | [5 empty] | 10 | 18E1C4 (5 Ton) | 505800 | 488600
Design Sensible Cooling Load | 2913.93 | BTU/h |  |  |  |  | 9 | 18E1C4 (5 Ton) | 449600 | 434300
Design Heating Load | 6657.87 | BTU/h |  |  |  |  | 8 | 18E1C4 (5 Ton) | 393400 | 380000
Sensible Capacity Derating (1) | 3.382% | [5 empty] | 7 | 18E1C4 (5 Ton) | 337200 | 325700
[7 empty] | 6 | 18E1C4 (5 Ton) | 281000 | 271400
Recommended Wall Packaged Unit | [6 empty] | 5 | 18E1C4 (5 Ton) | 224800 | 217100
Recommended Wall Pack Unit Quantity (2) | 2 |  | Sensible Capacity @ 95F ODT | 10500 | BTU/h |  | 4 | 18E1C4 (5 Ton) | 168600 | 162800
Recommended Wall Pack Unit Size | 3R1C1 (1 Ton) |  | De-rated Sensible Capacity | 10100 | BTU/h |  | 3 | 18E1C4 (5 Ton) | 112400 | 108500
Minimum Heater Size (3) | 2 | kW |  |  |  |  | 3 | 13E1C3 (3.5 Ton) | 81800 | 79000
[7 empty] | 2 | 18E1C4 (5 Ton) | 56200 | 54200
(1) HVAC sensible capacity is typically rated at 95°F outdoor temperature. When the outdoor temperature is greater than 95°F, HVAC derating needs to be taken into account when sizing units. | [6 empty] | 2 | 13E1C3 (3.5 Ton) | 40900 | 39500
(2) This recommended quantity includes +1 redundancy protection | [6 empty] | 2 | 9E1C2 (2.5 Ton) | 29600 | 28500
(3) Heater Size assumes constant equipment load. If equipment load is variable, use minimum equipment load to determine heater size. | [6 empty] | 2 | 7E1C2 (2 Ton) | 24200 | 23300
[7 empty] | 2 | 5R1C1 (1.5 Ton) | 15600 | 15000
[7 empty] | 2 | 3R1C1 (1 Ton) | 10500 | 10100

## Methodology
Formulas
Total Load
Where
Q = Load in Btu
ΔT = Temperature difference between inside and outside
k = constant, ≈ 1 BTU / ft^2 / °F / hr
A = Surface Area
R = Insulation R-Value
Heat Exchange due to Free Cooling/ Ventilation
Where
CFM = Air Volume in CFM
k1 = constant, ≈ 1.08 BTU /CFM / °F / hr
ΔT = Temperature difference between inside and outside